## Sheet1
Area | Flow | Consituent | Metric | Avg | PI Tag | Type | Description | Units | Range
NPRI1 | Inf | TSS | Conc | 7d | Primaries_NPRI1_InfTSSConc_7d | Integer | 7d average of NPRI1 influent TSS | mg/L | 0-100
NPRI1 | Eff | TSS | Conc | 7d | Primaries_NPRI1_EffTSSConc_7d | Integer | 7d average of NPRI1 effluent TSS | mg/L | 0-100
NPRI1 | Inf | TSS | Conc | 30d | Primaries_NPRI1_InfTSSConc_30d | Integer | 30d average of NPRI1 influent TSS | mg/L | 0-100
NPRI1 | Eff | TSS | Conc | 30d | Primaries_NPRI1_EffTSSConc_30d | Integer | 30d average of NPRI1 effluent TSS | mg/L | 0-100
NPRI1 | Inf | BOD | Conc | 7d | Primaries_NPRI1_InfBODConc_7d | Integer | 7d average of NPRI1 influent BOD | mg/L | 0-100
NPRI1 | Eff | BOD | Conc | 7d | Primaries_NPRI1_EffBODConc_7d | Integer | 7d average of NPRI1 effluent BOD | mg/L | 0-100
NPRI1 | Inf | BOD | Conc | 30d | Primaries_NPRI1_InfBODConc_30d | Integer | 30d average of NPRI1 influent BOD | mg/L | 0-100
NPRI1 | Eff | BOD | Conc | 30d | Primaries_NPRI1_EffBODConc_30d | Integer | 30d average of NPRI1 effluent BOD | mg/L | 0-100
NPRI1+2 | Inf | TSS | Load | 7d | Primaries_NPRI1+2_InfTSSLoad_7d | Float | 7d average of NPRI1+2 influent TSS load | t/d | 0-100
NPRI1+2 | Eff | TSS | Load | 7d | Primaries_NPRI1+2_EffTSSLoad_7d | Float | 7d average of NPRI1+2 effluent TSS load | t/d | 0-100
NPRI1+2 | Inf | TSS | Load | 30d | Primaries_NPRI1+2_InfTSSLoad_30d | Float | 30d average of NPRI1+2 influent TSS load | t/d | 0-100
NPRI1+2 | Eff | TSS | Load | 30d | Primaries_NPRI1+2_EffTSSLoad_30d | Float | 30d average of NPRI1+2 effluent TSS load | t/d | 0-100
NPRI1+2 | Inf | BOD | Load | 7d | Primaries_NPRI1+2_InfBODLoad_7d | Float | 7d average of NPRI1+2 influent BOD load | t/d | 0-100
NPRI1+2 | Eff | BOD | Load | 7d | Primaries_NPRI1+2_EffBODLoad_7d | Float | 7d average of NPRI1+2 effluent BOD load | t/d | 0-100
NPRI1+2 | Inf | BOD | Load | 30d | Primaries_NPRI1+2_InfBODLoad_30d | Float | 30d average of NPRI1+2 influent BOD load | t/d | 0-100
NPRI1+2 | Eff | BOD | Load | 30d | Primaries_NPRI1+2_EffBODLoad_30d | Float | 30d average of NPRI1+2 effluent BOD load | t/d | 0-100
NPRI1+2 | Inf | TSS | Removal | 7d | Primaries_NPRI1+2_InfTSSRemoval_7d | Integer | 7d average of NPRI1+2 influent TSSremoval | % | 0-100
NPRI1+2 | Eff | TSS | Removal | 7d | Primaries_NPRI1+2_EffTSSRemoval_7d | Integer | 7d average of NPRI1+2 effluent TSSremoval | % | 0-100
NPRI1+2 | Inf | TSS | Removal | 30d | Primaries_NPRI1+2_InfTSSRemoval_30d | Integer | 30d average of NPRI1+2 influent TSSremoval | % | 0-100
NPRI1+2 | Eff | TSS | Removal | 30d | Primaries_NPRI1+2_EffTSSRemoval_30d | Integer | 30d average of NPRI1+2 effluent TSSremoval | % | 0-100
NPRI1+2 | Inf | BOD | Removal | 7d | Primaries_NPRI1+2_InfBODRemoval_7d | Integer | 7d average of NPRI1+2 influent BODremoval | % | 0-100
NPRI1+2 | Eff | BOD | Removal | 7d | Primaries_NPRI1+2_EffBODRemoval_7d | Integer | 7d average of NPRI1+2 effluent BODremoval | % | 0-100
NPRI1+2 | Inf | BOD | Removal | 30d | Primaries_NPRI1+2_InfBODRemoval_30d | Integer | 30d average of NPRI1+2 influent BODremoval | % | 0-100
NPRI1+2 | Eff | BOD | Removal | 30d | Primaries_NPRI1+2_EffBODRemoval_30d | Integer | 30d average of NPRI1+2 effluent BODremoval | % | 0-100
NPRI1+2 | SOR |  |  | 1d | Primaries_NPRI1+2_SOR_1d | Float | NPRI1+2 surface overflow rate | gpd/ft2 | 400-1400
NPRI1+2 | SOR |  |  | 7d | Primaries_NPRI1+2_SOR_7d | Float | 7d average of NPRI1+2 surface overflow rate | gpd/ft2 | 400-1400
NPRI1+2 | SOR |  |  | 30d | Primaries_NPRI1+2_SOR_30d | Float | 30d average of NPRI1+2 surface overflow rate | gpd/ft2 | 400-1400
NPRI2 | Inf | TSS | Conc | 7d | Primaries_NPRI2_InfTSSConc_7d | Integer | 7d average of NPRI2 influent TSS | mg/L | 0-100
NPRI2 | Eff | TSS | Conc | 7d | Primaries_NPRI2_EffTSSConc_7d | Integer | 7d average of NPRI2 effluent TSS | mg/L | 0-100
NPRI2 | Inf | TSS | Conc | 30d | Primaries_NPRI2_InfTSSConc_30d | Integer | 30d average of NPRI2 influent TSS | mg/L | 0-100
NPRI2 | Eff | TSS | Conc | 30d | Primaries_NPRI2_EffTSSConc_30d | Integer | 30d average of NPRI2 effluent TSS | mg/L | 0-100
NPRI2 | Inf | BOD | Conc | 7d | Primaries_NPRI2_InfBODConc_7d | Integer | 7d average of NPRI2 influent BOD | mg/L | 0-100
NPRI2 | Eff | BOD | Conc | 7d | Primaries_NPRI2_EffBODConc_7d | Integer | 7d average of NPRI2 effluent BOD | mg/L | 0-100
NPRI2 | Inf | BOD | Conc | 30d | Primaries_NPRI2_InfBODConc_30d | Integer | 30d average of NPRI2 influent BOD | mg/L | 0-100
NPRI2 | Eff | BOD | Conc | 30d | Primaries_NPRI2_EffBODConc_30d | Integer | 30d average of NPRI2 effluent BOD | mg/L | 0-100
NPRI3 | Inf | TSS | Conc | 7d | Primaries_NPRI3_InfTSSConc_7d | Integer | 7d average of NPRI3 influent TSS | mg/L | 0-100
NPRI3 | Eff | TSS | Conc | 7d | Primaries_NPRI3_EffTSSConc_7d | Integer | 7d average of NPRI3 effluent TSS | mg/L | 0-100
NPRI3 | Inf | TSS | Conc | 30d | Primaries_NPRI3_InfTSSConc_30d | Integer | 30d average of NPRI3 influent TSS | mg/L | 0-100
NPRI3 | Eff | TSS | Conc | 30d | Primaries_NPRI3_EffTSSConc_30d | Integer | 30d average of NPRI3 effluent TSS | mg/L | 0-100
NPRI3 | Inf | BOD | Conc | 7d | Primaries_NPRI3_InfBODConc_7d | Integer | 7d average of NPRI3 influent BOD | mg/L | 0-100
NPRI3 | Eff | BOD | Conc | 7d | Primaries_NPRI3_EffBODConc_7d | Integer | 7d average of NPRI3 effluent BOD | mg/L | 0-100
NPRI3 | Inf | BOD | Conc | 30d | Primaries_NPRI3_InfBODConc_30d | Integer | 30d average of NPRI3 influent BOD | mg/L | 0-100
NPRI3 | Eff | BOD | Conc | 30d | Primaries_NPRI3_EffBODConc_30d | Integer | 30d average of NPRI3 effluent BOD | mg/L | 0-100
NPRI3 | Inf | TSS | Load | 7d | Primaries_NPRI3_InfTSSLoad_7d | Float | 7d average of NPRI3 influent TSS load | t/d | 0-100
NPRI3 | Eff | TSS | Load | 7d | Primaries_NPRI3_EffTSSLoad_7d | Float | 7d average of NPRI3 effluent TSS load | t/d | 0-100
NPRI3 | Inf | TSS | Load | 30d | Primaries_NPRI3_InfTSSLoad_30d | Float | 30d average of NPRI3 influent TSS load | t/d | 0-100
NPRI3 | Eff | TSS | Load | 30d | Primaries_NPRI3_EffTSSLoad_30d | Float | 30d average of NPRI3 effluent TSS load | t/d | 0-100
NPRI3 | Inf | BOD | Load | 7d | Primaries_NPRI3_InfBODLoad_7d | Float | 7d average of NPRI3 influent BOD load | t/d | 0-100
NPRI3 | Eff | BOD | Load | 7d | Primaries_NPRI3_EffBODLoad_7d | Float | 7d average of NPRI3 effluent BOD load | t/d | 0-100
NPRI3 | Inf | BOD | Load | 30d | Primaries_NPRI3_InfBODLoad_30d | Float | 30d average of NPRI3 influent BOD load | t/d | 0-100
NPRI3 | Eff | BOD | Load | 30d | Primaries_NPRI3_EffBODLoad_30d | Float | 30d average of NPRI3 effluent BOD load | t/d | 0-100
NPRI3 | Inf | TSS | Removal | 7d | Primaries_NPRI3_InfTSSRemoval_7d | Integer | 7d average of NPRI3 influent TSSremoval | % | 0-100
NPRI3 | Eff | TSS | Removal | 7d | Primaries_NPRI3_EffTSSRemoval_7d | Integer | 7d average of NPRI3 effluent TSSremoval | % | 0-100
NPRI3 | Inf | TSS | Removal | 30d | Primaries_NPRI3_InfTSSRemoval_30d | Integer | 30d average of NPRI3 influent TSSremoval | % | 0-100
NPRI3 | Eff | TSS | Removal | 30d | Primaries_NPRI3_EffTSSRemoval_30d | Integer | 30d average of NPRI3 effluent TSSremoval | % | 0-100
NPRI3 | Inf | BOD | Removal | 7d | Primaries_NPRI3_InfBODRemoval_7d | Integer | 7d average of NPRI3 influent BODremoval | % | 0-100
NPRI3 | Eff | BOD | Removal | 7d | Primaries_NPRI3_EffBODRemoval_7d | Integer | 7d average of NPRI3 effluent BODremoval | % | 0-100
NPRI3 | Inf | BOD | Removal | 30d | Primaries_NPRI3_InfBODRemoval_30d | Integer | 30d average of NPRI3 influent BODremoval | % | 0-100
NPRI3 | Eff | BOD | Removal | 30d | Primaries_NPRI3_EffBODRemoval_30d | Integer | 30d average of NPRI3 effluent BODremoval | % | 0-100
NPRI3 | SOR |  |  | 1d | Primaries_NPRI3_SOR_1d | Float | NPRI3 surface overflow rate | gpd/ft2 | 400-1400
NPRI3 | SOR |  |  | 7d | Primaries_NPRI3_SOR_7d | Float | 7d average of NPRI3 surface overflow rate | gpd/ft2 | 400-1400
NPRI3 | SOR |  |  | 30d | Primaries_NPRI3_SOR_30d | Float | 30d average of NPRI3 surface overflow rate | gpd/ft2 | 400-1400
SPRI | Inf | TSS | Conc | 7d | Primaries_SPRI_InfTSSConc_7d | Integer | 7d average of SPRI influent TSS | mg/L | 0-100
SPRI | Eff | TSS | Conc | 7d | Primaries_SPRI_EffTSSConc_7d | Integer | 7d average of SPRI effluent TSS | mg/L | 0-100
SPRI | Inf | TSS | Conc | 30d | Primaries_SPRI_InfTSSConc_30d | Integer | 30d average of SPRI influent TSS | mg/L | 0-100
SPRI | Eff | TSS | Conc | 30d | Primaries_SPRI_EffTSSConc_30d | Integer | 30d average of SPRI effluent TSS | mg/L | 0-100
SPRI | Inf | BOD | Conc | 7d | Primaries_SPRI_InfBODConc_7d | Integer | 7d average of SPRI influent BOD | mg/L | 0-100
SPRI | Eff | BOD | Conc | 7d | Primaries_SPRI_EffBODConc_7d | Integer | 7d average of SPRI effluent BOD | mg/L | 0-100
SPRI | Inf | BOD | Conc | 30d | Primaries_SPRI_InfBODConc_30d | Integer | 30d average of SPRI influent BOD | mg/L | 0-100
SPRI | Eff | BOD | Conc | 30d | Primaries_SPRI_EffBODConc_30d | Integer | 30d average of SPRI effluent BOD | mg/L | 0-100
SPRI | Inf | TSS | Load | 7d | Primaries_SPRI_InfTSSLoad_7d | Float | 7d average of SPRI influent TSS load | t/d | 0-100
SPRI | Eff | TSS | Load | 7d | Primaries_SPRI_EffTSSLoad_7d | Float | 7d average of SPRI effluent TSS load | t/d | 0-100
SPRI | Inf | TSS | Load | 30d | Primaries_SPRI_InfTSSLoad_30d | Float | 30d average of SPRI influent TSS load | t/d | 0-100
SPRI | Eff | TSS | Load | 30d | Primaries_SPRI_EffTSSLoad_30d | Float | 30d average of SPRI effluent TSS load | t/d | 0-100
SPRI | Inf | BOD | Load | 7d | Primaries_SPRI_InfBODLoad_7d | Float | 7d average of SPRI influent BOD load | t/d | 0-100
SPRI | Eff | BOD | Load | 7d | Primaries_SPRI_EffBODLoad_7d | Float | 7d average of SPRI effluent BOD load | t/d | 0-100
SPRI | Inf | BOD | Load | 30d | Primaries_SPRI_InfBODLoad_30d | Float | 30d average of SPRI influent BOD load | t/d | 0-100
SPRI | Eff | BOD | Load | 30d | Primaries_SPRI_EffBODLoad_30d | Float | 30d average of SPRI effluent BOD load | t/d | 0-100
SPRI | Inf | TSS | Removal | 7d | Primaries_SPRI_InfTSSRemoval_7d | Integer | 7d average of SPRI influent TSSremoval | % | 0-100
SPRI | Eff | TSS | Removal | 7d | Primaries_SPRI_EffTSSRemoval_7d | Integer | 7d average of SPRI effluent TSSremoval | % | 0-100
SPRI | Inf | TSS | Removal | 30d | Primaries_SPRI_InfTSSRemoval_30d | Integer | 30d average of SPRI influent TSSremoval | % | 0-100
SPRI | Eff | TSS | Removal | 30d | Primaries_SPRI_EffTSSRemoval_30d | Integer | 30d average of SPRI effluent TSSremoval | % | 0-100
SPRI | Inf | BOD | Removal | 7d | Primaries_SPRI_InfBODRemoval_7d | Integer | 7d average of SPRI influent BODremoval | % | 0-100
SPRI | Eff | BOD | Removal | 7d | Primaries_SPRI_EffBODRemoval_7d | Integer | 7d average of SPRI effluent BODremoval | % | 0-100
SPRI | Inf | BOD | Removal | 30d | Primaries_SPRI_InfBODRemoval_30d | Integer | 30d average of SPRI influent BODremoval | % | 0-100
SPRI | Eff | BOD | Removal | 30d | Primaries_SPRI_EffBODRemoval_30d | Integer | 30d average of SPRI effluent BODremoval | % | 0-100
SPRI | SOR |  |  | 1d | Primaries_SPRI_SOR_1d | Float | SPRI surface overflow rate | gpd/ft2 | 400-1400
SPRI | SOR |  |  | 7d | Primaries_SPRI_SOR_7d | Float | 7d average of SPRI surface overflow rate | gpd/ft2 | 400-1400
SPRI | SOR |  |  | 30d | Primaries_SPRI_SOR_30d | Float | 30d average of SPRI surface overflow rate | gpd/ft2 | 400-1400