## Sheet1
North Disinfection HRT Calculation
Parameter | Value | Units | Notes | Flow (MGD) | HRT (min) | Predicted HRT | % Diff
Flow | 54.11 | MGD |  | 20 | 159.4 | 155.9374 | -2.172%
| 83.7082 | cfs |  | 25 | 127.8 | 125.9808 | -1.423%
Determine Water Surface Elevation at Weir |  |  |  | 30 | 106.7 | 105.8296 | -0.8158%
Banana Weir Elev. | 5109.8 | ft | Contact basin effluent weir | 35 | 91.7 | 91.3284 | -0.4052%
Banana Weir Length | 91 | ft |  | 40 | 80.4 | 80.3833 | -0.02082%
Weir Coefficient | 3.33 |  |  | 45 | 71.7 | 71.823 | 0.1716%
Weir Head | 0.42415 | ft | Freefall Discharge, Q1=C*L*H^1.5 | 50 | 64.7 | 64.9411 | 0.3726%
| 5.0898 | in |  | 55 | 58.9 | 59.2855 | 0.6544%
Water Surface Elev. | 5110.2242 | ft |  | 60 | 54.1 | 54.5535 | 0.8382%
Determine Contact Basin Average Depth |  |  |  | 65 | 50 | 50.5347 | 1.069%
WS EL Correction @ Low Flows | 0 | ft |  | 70 | 46.5 | 47.0784 | 1.244%
WS EL Correction @ MMF (106 MGD) | 0.1 | ft | Apply to flows greater than or equal to 100 MGD | 75 | 43.5 | 44.0734 | 1.318%
WS EL Correction @ PHF (144 MGD) | 0.3 | ft | Apply to flows greater than or equal to 140 MGD | 80 | 40.8 | 41.4363 | 1.56%
WS EL Correction @ PIF (200 MGD) | 0.5 | ft |  | 85 | 38.5 | 39.103 | 1.566%
Corrected WS EL | 5110.2242 | ft | Adjust the correction based on the flow input | 90 | 36.42 | 37.0236 | 1.657%
CCB Floor Elev. | 5096.8 | ft |  | 95 | 34.57 | 35.1586 | 1.703%
CCB Average Depth | 13.4242 | ft |  | 100 | 33.15 | 33.4761 | 0.9837%
Determine Contact Basin HRT |  |  |  | 105 | 31.61 | 31.9505 | 1.077%
CCB Surface Area | 21770 | sf | Determined from Drawing C-2 (PAR 302) | 110 | 30.27 | 30.5607 | 0.9604%
Contact Basin Vol | 2.186 | Mgal |  | 115 | 28.93 | 29.2892 | 1.242%
Contact Basin HRT | 58.1744 | min |  | 120 | 27.8 | 28.1214 | 1.156%
Determine Influent Conduit Average Depth |  |  |  | 125 | 26.77 | 27.0451 | 1.028%
WS EL Correction @ Low Flows | 0.6 | ft |  | 130 | 25.74 | 26.0498 | 1.204%
WS EL Correction @ MMF (106 MGD) | 0.8 | ft | Apply to flows greater than or equal to 100 MGD | 135 | 24.82 | 25.1267 | 1.236%
WS EL Correction @ PHF (144 MGD) | 1 | ft | Apply to flows greater than or equal to 140 MGD | 140 | 24.32 | 24.2681 | -0.2132%
WS EL Correction @ PIF (200 MGD) | 1.2 | ft | Apply to flows greater than or equal to 190 MGD | 145 | 23.5 | 23.4675 | -0.1382%
Corrected WS EL | 5110.8242 | ft | Adjust the correction based on the flow input | 150 | 22.78 | 22.7191 | -0.2672%
Influent Conduit (Sloped Section) Upstream Floor Elev. | 5107 | ft |  | 155 | 22.06 | 22.018 | -0.1904%
Influent Conduit (Sloped Section) Downstream Floor Elev. | 5100 | ft |  | 160 | 21.44 | 21.3598 | -0.3743%
Influent Conduit (Sloped Section) Average Depth, Area 1 | 3.5 | ft | If WS EL is greater than 5107, this depth is fixed at 3.5 ft | 165 | 20.82 | 20.7406 | -0.3816%
Influent Conduit (Sloped Section) Average Depth, Area 2 | 3.8242 | ft | Additional depth above 5107, total max depth = 9.5 ft (fully submerged) | 170 | 20.2 | 20.157 | -0.2129%
Influent Conduit (Horiz. Curve Section) Floor Elev. | 5100 | ft |  | 175 | 19.69 | 19.6061 | -0.4262%
Influent Conduit (Horiz. Curve Section) Depth | 10.8242 | ft | Max depth = 13 ft (fully submerged) | 180 | 19.17 | 19.0851 | -0.4429%
Determine Influent Conduit HRT |  |  |  | 185 | 18.66 | 18.5917 | -0.3661%
Influent Conduit (Sloped Section) SA | 685 | sf | Determined from Drawing C-4 (PAR 302) | 190 | 18.47 | 18.1237 | -1.875%
Influent Conduit Vol, Area 1 | 17933.3 | gal |  | 195 | 17.95 | 17.6792 | -1.509%
Influent Conduit Vol, Area 2 | 19594.1898 | gal |  | 200 | 17.54 | 17.2564 | -1.617%
Influent Conduit (Horiz. Curve Section) SA | 306 | sf | Determined from Drawing C-4 (PAR 302)
Influent Conduit (Horiz. Curve Section) Vol | 24775.1849 | gal
Influent Conduit Vol, Total | 62302.6748 | gal
Influent Conduit HRT | 1.658 | min
Determine HRT from Applied Dose to Sample Locations
Volume to 1-min grab location 012_712_1011 | 0.1095 | Mgal | Influent conduit plus static mixer location
HRT to 1-min grab location | 2.914 | min
Volume to 10-min grab location 012_712_1012 | 0.85355 | Mgal | Influent conduit plus static mixer plus first pass
HRT to 10-min grab location | 22.7152 | min
Volume to 20-min grab location 012_712_1013 | 1.5509 | Mgal | Influent conduit plus static mixer plus first and second passes
HRT to 20-min grab location | 41.2738 | min
Volume to 30-min grab location 012_712_1021 | 2.2483 | Mgal | Influent conduit plus total contact basin
HRT to 30-min grab location | 59.8324 | min | Actual sample location is downstream of weir, consider adding 1 min
Volume to online analyzer (AI_K826) location | 0.28622 | Mgal
HRT to online analyzer location | 7.6171 | min
Volume to 1/2-basin location | 1.2022 | Mgal | Influent conduit plus static mixer plus first pass and half of second pass
HRT to 1/2-basin location | 31.9945 | min
Note on G2: Freedman, Dan: HRT from applied dose