## Sheet1
North Disinfection HRT Calculation
Parameter | Value | Units | Notes | Flow (MGD) | HRT (min) | Predicted HRT | % Diff | HRT 1 min | HRT 1/2 basin
Flow | 20 | MGD |  | 20 | 159.4 | 155.9374 | -2.172% | 7.7219 | 85.1937
| 30.94 | cfs |  | 25 | 127.8 | 125.9808 | -1.423%
Determine Water Surface Elevation at Weir |  |  |  | 30 | 106.7 | 105.8296 | -0.8158% | 5.1835 | 57.0963
Banana Weir Elev. | 5109.8 | ft | Contact basin effluent weir | 35 | 91.7 | 91.3284 | -0.4052%
Banana Weir Length | 91 | ft |  | 40 | 80.4 | 80.3833 | -0.02082% | 3.9114 | 43.0233
Weir Coefficient | 3.33 |  |  | 45 | 71.7 | 71.823 | 0.1716%
Weir Head | 0.21845 | ft | Freefall Discharge, Q1=C*L*H^1.5 | 50 | 64.7 | 64.9411 | 0.3726% | 3.1467 | 34.5666
| 2.6214 | in |  | 55 | 58.9 | 59.2855 | 0.6544%
Water Surface Elev. | 5110.0185 | ft |  | 60 | 54.1 | 54.5535 | 0.8382% | 2.6359 | 28.9207
Determine Contact Basin Average Depth |  |  |  | 65 | 50 | 50.5347 | 1.069%
WS EL Correction @ Low Flows | 0 | ft |  | 70 | 46.5 | 47.0784 | 1.244%
WS EL Correction @ MMF (106 MGD) | 0.1 | ft | Apply to flows greater than or equal to 100 MGD | 75 | 43.5 | 44.0734 | 1.318%
WS EL Correction @ PHF (144 MGD) | 0.3 | ft | Apply to flows greater than or equal to 140 MGD | 80 | 40.8 | 41.4363 | 1.56%
WS EL Correction @ PIF (200 MGD) | 0.5 | ft |  | 85 | 38.5 | 39.103 | 1.566%
Corrected WS EL | 5110.0185 | ft | Adjust the correction based on the flow input | 90 | 36.42 | 37.0236 | 1.657%
CCB Floor Elev. | 5096.8 | ft |  | 95 | 34.57 | 35.1586 | 1.703%
CCB Average Depth | 13.2185 | ft |  | 100 | 33.15 | 33.4761 | 0.9837% | 1.6476 | 17.7518
Determine Contact Basin HRT |  |  |  | 105 | 31.61 | 31.9505 | 1.077%
CCB Surface Area | 21770 | sf | Determined from Drawing C-2 (PAR 302) | 110 | 30.27 | 30.5607 | 0.9604%
Contact Basin Vol | 2.1525 | Mgal |  | 115 | 28.93 | 29.2892 | 1.242%
Contact Basin HRT | 154.9791 | min |  | 120 | 27.8 | 28.1214 | 1.156%
Determine Influent Conduit Average Depth |  |  |  | 125 | 26.77 | 27.0451 | 1.028%
WS EL Correction @ Low Flows | 0.6 | ft |  | 130 | 25.74 | 26.0498 | 1.204%
WS EL Correction @ MMF (106 MGD) | 0.8 | ft | Apply to flows greater than or equal to 100 MGD | 135 | 24.82 | 25.1267 | 1.236%
WS EL Correction @ PHF (144 MGD) | 1 | ft | Apply to flows greater than or equal to 140 MGD | 140 | 24.32 | 24.2681 | -0.2132%
WS EL Correction @ PIF (200 MGD) | 1.2 | ft | Apply to flows greater than or equal to 190 MGD | 145 | 23.5 | 23.4675 | -0.1382%
Corrected WS EL | 5110.6185 | ft | Adjust the correction based on the flow input | 150 | 22.78 | 22.7191 | -0.2672% | 1.1544 | 12.2018
Influent Conduit (Sloped Section) Upstream Floor Elev. | 5107 | ft |  | 155 | 22.06 | 22.018 | -0.1904%
Influent Conduit (Sloped Section) Downstream Floor Elev. | 5100 | ft |  | 160 | 21.44 | 21.3598 | -0.3743%
Influent Conduit (Sloped Section) Average Depth, Area 1 | 3.5 | ft | If WS EL is greater than 5107, this depth is fixed at 3.5 ft | 165 | 20.82 | 20.7406 | -0.3816%
Influent Conduit (Sloped Section) Average Depth, Area 2 | 3.6185 | ft | Additional depth above 5107, total max depth = 9.5 ft (fully submerged) | 170 | 20.2 | 20.157 | -0.2129%
Influent Conduit (Horiz. Curve Section) Floor Elev. | 5100 | ft |  | 175 | 19.69 | 19.6061 | -0.4262%
Influent Conduit (Horiz. Curve Section) Depth | 10.6185 | ft | Max depth = 13 ft (fully submerged) | 180 | 19.17 | 19.0851 | -0.4429%
Determine Influent Conduit HRT |  |  |  | 185 | 18.66 | 18.5917 | -0.3661%
Influent Conduit (Sloped Section) SA | 685 | sf | Determined from Drawing C-4 (PAR 302) | 190 | 18.47 | 18.1237 | -1.875%
Influent Conduit Vol, Area 1 | 17933.3 | gal |  | 195 | 17.95 | 17.6792 | -1.509%
Influent Conduit Vol, Area 2 | 18540.2255 | gal |  | 200 | 17.54 | 17.2564 | -1.617% | 0.90615 | 9.4126
Influent Conduit (Horiz. Curve Section) SA | 306 | sf | Determined from Drawing C-4 (PAR 302)
Influent Conduit (Horiz. Curve Section) Vol | 24304.3629 | gal
Influent Conduit Vol, Total | 60777.8884 | gal
Influent Conduit HRT | 4.376 | min
Determine HRT from Applied Dose to Sample Locations
Volume to 1-min grab location 012_712_1011 | 0.10725 | Mgal | Influent conduit plus static mixer location
HRT to 1-min grab location | 7.7219 | min
Volume to 10-min grab location 012_712_1012 | 0.83991 | Mgal | Influent conduit plus static mixer plus first pass
HRT to 10-min grab location | 60.4732 | min
Volume to 20-min grab location 012_712_1013 | 1.5266 | Mgal | Influent conduit plus static mixer plus first and second passes
HRT to 20-min grab location | 109.9141 | min
Volume to 30-min grab location 012_712_1021 | 2.2133 | Mgal | Influent conduit plus total contact basin
HRT to 30-min grab location | 159.3551 | min | Actual sample location is downstream of weir, consider adding 1 min
Volume to online analyzer (AI_K826) location | 0.28127 | Mgal
HRT to online analyzer location | 20.2512 | min
Volume to 1/2-basin location | 1.1832 | Mgal | Influent conduit plus static mixer plus first pass and half of second pass
HRT to 1/2-basin location | 85.1937 | min
Note on G2: Freedman, Dan: HRT from applied dose