## Copy of PAA PROFILE DATA_6-27-1
LOCATION_CODE | COMMON_NAME | LOCATION_DESCRIPTION | COLLECTION_DATE | COLLECTION_TIME | COLLECTION_DATETIME | ANALYSIS_CODE | ANALYSIS_NAME | ANALYTE_NAME | COMBINATION_RESULT | NUMERIC_RESULT | ANALYSIS_UNIT | ANALYTE_MDL | QUALIFIER | ACQUIRED_TYPE | Chemscan PAA | Actual PAA | Difference | Flow |  | Chemscan PAA
012_712_1011 | N_PAA1MIN | RWH North, Post-PAA addition, 1 Min Contact Time | 2019-06-23 | 06:36 | 6/23/19 06:36 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 1.0 | 1.0 | mg/L | 0.1 |  | G | 0.88846 | 1.0 | 0.11154 | 38.7479 | 2019-06-22 06:00 | 0.70047
012_700_1011 | N_PREPAA | RWH North, Pre-PAA addition | 2019-06-23 | 06:34 | 6/23/19 06:34 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 10500 | 10500 | EC/100mL | 100 |  | G |  |  |  |  | 2019-06-22 06:01 | 0.70047
011_530_1061 | S_PREPAA | RWH South, Sec Clarifiers, Clar 6 Eff | 2019-06-23 | 06:30 | 6/23/19 06:30 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 77000 | 77000 | EC/100mL | 100 |  | G |  |  |  |  | 2019-06-22 06:02 | 0.70047
012_712_1011 | N_PAA1MIN | RWH North, Post-PAA addition, 1 Min Contact Time | 2019-06-23 | 06:36 | 6/23/19 06:36 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | Scratched |  | mg/L | 0.1 | -5 | G |  |  |  |  | 2019-06-22 06:03 | 0.70047
012_700_1011 | N_PREPAA | RWH North, Pre-PAA addition | 2019-06-23 | 06:34 | 6/23/19 06:34 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | Scratched |  | EC/100mL | 1 | -5 | G |  |  |  |  | 2019-06-22 06:04 | 0.70047
011_530_1061 | S_PREPAA | RWH South, Sec Clarifiers, Clar 6 Eff | 2019-06-23 | 06:30 | 6/23/19 06:30 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | Scratched |  | EC/100mL | 1 | -5 | G |  |  |  |  | 2019-06-22 06:05 | 0.71507
012_712_1012 | 1 NPAA10MN | RWH North, Post-PAA addition, 10 Min Contact Time | 2019-06-24 | 07:46 | 6/24/19 07:46 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.46 | 0.46 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 06:06 | 0.77424
012_712_1012 | 1 NPAA10MN | RWH North, Post-PAA addition, 10 Min Contact Time | 2019-06-24 | 07:46 | 6/24/19 07:46 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 41 | 41 | EC/100mL | 1 |  | G |  |  |  |  | 2019-06-22 06:07 | 0.77539
012_712_1011 | 1 NPAA1MIN | RWH North, Post-PAA addition, 1 Min Contact Time | 2019-06-24 | 07:42 | 6/24/19 07:42 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 1.18 | 1.18 | mg/L | 0.1 |  | G | 0.83948 | 1.18 | 0.34052 | 37.7045 | 2019-06-22 06:08 | 0.77539
012_712_1011 | 1 NPAA1MIN | RWH North, Post-PAA addition, 1 Min Contact Time | 2019-06-24 | 07:42 | 6/24/19 07:42 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 6630 | 6630 | EC/100mL | 100 |  | G |  |  |  |  | 2019-06-22 06:09 | 0.77539
012_712_1013 | 1 NPAA20MN | RWH North, Post-PAA addition, 20 Min Contact Time | 2019-06-24 | 07:49 | 6/24/19 07:49 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.21 | 0.21 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 06:10 | 0.76542
012_712_1021 | 1 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-24 | 07:54 | 6/24/19 07:54 | TSS | Total Suspended Solids | Total Suspended Solids | 4 | 4 | mg/L | 1 |  | G |  |  |  |  | 2019-06-22 06:11 | 0.74879
012_712_1021 | 1 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-24 | 07:54 | 6/24/19 07:54 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 40 | 40 | EC/100mL | 1 |  | G |  |  |  |  | 2019-06-22 06:12 | 0.73217
012_712_1021 | 1 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-24 | 07:54 | 6/24/19 07:54 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.00 | 0.00 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 06:13 | 0.73045
012_712_1012 | 2 NPAA10MN | RWH North, Post-PAA addition, 10 Min Contact Time | 2019-06-24 | 11:02 | 6/24/19 11:02 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.85 | 0.85 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 06:14 | 0.73045
012_712_1012 | 2 NPAA10MN | RWH North, Post-PAA addition, 10 Min Contact Time | 2019-06-24 | 11:02 | 6/24/19 11:02 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 222 | 222 | EC/100mL | 1 |  | G |  |  |  |  | 2019-06-22 06:15 | 0.73045
012_712_1011 | 2 NPAA1MIN | RWH North, Post-PAA addition, 1 Min Contact Time | 2019-06-24 | 10:57 | 6/24/19 10:57 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 1.21 | 1.21 | mg/L | 0.1 |  | G | 0.85212 | 1.21 | 0.35788 | 86.2817 | 2019-06-22 06:16 | 0.73045
012_712_1011 | 2 NPAA1MIN | RWH North, Post-PAA addition, 1 Min Contact Time | 2019-06-24 | 10:57 | 6/24/19 10:57 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 4650 | 4650 | EC/100mL | 100 |  | G |  |  |  |  | 2019-06-22 06:17 | 0.73045
012_712_1013 | 2 NPAA20MN | RWH North, Post-PAA addition, 20 Min Contact Time | 2019-06-24 | 11:06 | 6/24/19 11:06 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.71 | 0.71 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 06:18 | 0.73045
012_712_1021 | 2 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-24 | 11:12 | 6/24/19 11:12 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.47 | 0.47 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 06:19 | 0.86213
012_712_1021 | 2 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-24 | 11:12 | 6/24/19 11:12 | TSS | Total Suspended Solids | Total Suspended Solids | 9 | 9 | mg/L | 1 |  | G |  |  |  |  | 2019-06-22 06:20 | 0.86213
012_712_1021 | 2 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-24 | 11:12 | 6/24/19 11:12 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 36 | 36 | EC/100mL | 1 |  | G |  |  |  |  | 2019-06-22 06:21 | 0.8654
012_700_1011 | 2 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-24 | 10:53 | 6/24/19 10:53 | CODLL | CODLL, w/Ag2SO4, w/ HgSO4 | CODLL, w/Ag2SO4, w/ HgSO4 | 21 | 21 | mg/L | 5 |  | G |  |  |  |  | 2019-06-22 06:22 | 0.87404
012_700_1011 | 2 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-24 | 10:53 | 6/24/19 10:53 | DTRM4 | Dig., Tot. Rec. Metals | Dig., Tot. Rec. Metals | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 06:23 | 0.88268
012_700_1011 | 2 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-24 | 10:53 | 6/24/19 10:53 | $ICPT1 | Metals, Tot., ICP | Metals, Tot., ICP | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 06:24 | 0.89131
012_700_1011 | 2 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-24 | 10:53 | 6/24/19 10:53 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 8570 | 8570 | EC/100mL | 100 |  | G |  |  |  |  | 2019-06-22 06:25 | 0.89395
012_700_1011 | 2 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-24 | 10:53 | 6/24/19 10:53 | TSS | Total Suspended Solids | Total Suspended Solids | 10 | 10 | mg/L | 1 |  | G |  |  |  |  | 2019-06-22 06:26 | 0.89395
012_712_1012 | 3 NPAA10MN | RWH North, Post-PAA addition, 10 Min Contact Time | 2019-06-24 | 13:05 | 6/24/19 13:05 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 1.07 | 1.07 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 06:27 | 0.89395
012_712_1012 | 3 NPAA10MN | RWH North, Post-PAA addition, 10 Min Contact Time | 2019-06-24 | 13:05 | 6/24/19 13:05 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 461 | 461 | EC/100mL | 1 |  | G |  |  |  |  | 2019-06-22 06:28 | 0.89395
012_712_1011 | 3 NPAA1MIN | RWH North, Post-PAA addition, 1 Min Contact Time | 2019-06-24 | 13:02 | 6/24/19 13:02 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 1.29 | 1.29 | mg/L | 0.1 |  | G | 0.99466 | 1.29 | 0.29534 | 100.1685 | 2019-06-22 06:29 | 0.89395
012_712_1011 | 3 NPAA1MIN | RWH North, Post-PAA addition, 1 Min Contact Time | 2019-06-24 | 13:02 | 6/24/19 13:02 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 9590 | 9590 | EC/100mL | 100 |  | G |  |  |  |  | 2019-06-22 06:30 | 0.89395
012_712_1013 | 3 NPAA20MN | RWH North, Post-PAA addition, 20 Min Contact Time | 2019-06-24 | 13:10 | 6/24/19 13:10 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.93 | 0.93 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 06:31 | 0.85249
012_712_1021 | 3 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-24 | 13:15 | 6/24/19 13:15 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 35 | 35 | EC/100mL | 1 |  | G |  |  |  |  | 2019-06-22 06:32 | 0.85217
012_712_1021 | 3 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-24 | 13:15 | 6/24/19 13:15 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.57 | 0.57 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 06:33 | 0.85186
012_712_1021 | 3 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-24 | 13:15 | 6/24/19 13:15 | TSS | Total Suspended Solids | Total Suspended Solids | 8 | 8 | mg/L | 1 |  | G |  |  |  |  | 2019-06-22 06:34 | 0.85155
012_700_1011 | 3 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-24 | 12:57 | 6/24/19 12:57 | CODLL | CODLL, w/Ag2SO4, w/ HgSO4 | CODLL, w/Ag2SO4, w/ HgSO4 | 23 | 23 | mg/L | 5 |  | G |  |  |  |  | 2019-06-22 06:35 | 0.85123
012_700_1011 | 3 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-24 | 12:57 | 6/24/19 12:57 | DTRM4 | Dig., Tot. Rec. Metals | Dig., Tot. Rec. Metals | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 06:36 | 0.85092
012_700_1011 | 3 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-24 | 12:57 | 6/24/19 12:57 | $ICPT1 | Metals, Tot., ICP | Metals, Tot., ICP | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 06:37 | 0.78492
012_700_1011 | 3 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-24 | 12:57 | 6/24/19 12:57 | TSS | Total Suspended Solids | Total Suspended Solids | 8 | 8 | mg/L | 1 |  | G |  |  |  |  | 2019-06-22 06:38 | 0.78492
012_700_1011 | 3 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-24 | 12:57 | 6/24/19 12:57 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 8890 | 8890 | EC/100mL | 100 |  | G |  |  |  |  | 2019-06-22 06:39 | 0.78492
011_530_1061 | S_PREPAA | RWH South, Sec Clarifiers, Clar 6 Eff | 2019-06-24 | 12:25 | 6/24/19 12:25 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 46100 | 46100 | EC/100mL | 100 |  | G |  |  |  |  | 2019-06-22 06:40 | 0.78492
012_712_1012 | 1 NPAA10MN | RWH North, Post-PAA addition, 10 Min Contact Time | 2019-06-25 | 08:04 | 6/25/19 08:04 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.58 | 0.58 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 06:41 | 0.78492
012_712_1012 | 1 NPAA10MN | RWH North, Post-PAA addition, 10 Min Contact Time | 2019-06-25 | 08:04 | 6/25/19 08:04 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 50 | 50 | EC/100mL | 1 |  | G |  |  |  |  | 2019-06-22 06:42 | 0.78492
012_712_1011 | 1 NPAA1MIN | RWH North, Post-PAA addition, 1 Min Contact Time | 2019-06-25 | 07:56 | 6/25/19 07:56 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 1.09 | 1.09 | mg/L | 0.1 |  | G | 0.69897 | 1.09 | 0.39103 | 38.6851 | 2019-06-22 06:43 | 0.70413
012_712_1011 | 1 NPAA1MIN | RWH North, Post-PAA addition, 1 Min Contact Time | 2019-06-25 | 07:56 | 6/25/19 07:56 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 8390 | 8390 | EC/100mL | 100 |  | G |  |  |  |  | 2019-06-22 06:44 | 0.70413
012_712_1013 | 1 NPAA20MN | RWH North, Post-PAA addition, 20 Min Contact Time | 2019-06-25 | 08:10 | 6/25/19 08:10 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.16 | 0.16 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 06:45 | 0.70413
012_712_1021 | 1 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-25 | 08:18 | 6/25/19 08:18 | TSS | Total Suspended Solids | Total Suspended Solids | 5 | 5 | mg/L | 1 |  | G |  |  |  |  | 2019-06-22 06:46 | 0.70413
012_712_1021 | 1 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-25 | 08:18 | 6/25/19 08:18 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 24 | 24 | EC/100mL | 1 |  | G |  |  |  |  | 2019-06-22 06:47 | 0.70413
012_712_1021 | 1 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-25 | 08:18 | 6/25/19 08:18 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.03 | 0.03 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 06:48 | 0.73697
012_712_1012 | 2 NPAA10MN | RWH North, Post-PAA addition, 10 Min Contact Time | 2019-06-25 | 11:10 | 6/25/19 11:10 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.70 | 0.70 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 06:49 | 0.7962
012_712_1012 | 2 NPAA10MN | RWH North, Post-PAA addition, 10 Min Contact Time | 2019-06-25 | 11:10 | 6/25/19 11:10 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 163 | 163 | EC/100mL | 1 |  | G |  |  |  |  | 2019-06-22 06:50 | 0.79588
012_712_1011 | 2 NPAA1MIN | RWH North, Post-PAA addition, 1 Min Contact Time | 2019-06-25 | 11:04 | 6/25/19 11:04 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 1.24 | 1.24 | mg/L | 0.1 |  | G | 0.70047 | 1.24 | 0.53953 | 82.1014 | 2019-06-22 06:51 | 0.79557
012_712_1011 | 2 NPAA1MIN | RWH North, Post-PAA addition, 1 Min Contact Time | 2019-06-25 | 11:04 | 6/25/19 11:04 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 11100 | 11100 | EC/100mL | 100 |  | G |  |  |  |  | 2019-06-22 06:52 | 0.79525
012_712_1013 | 2 NPAA20MN | RWH North, Post-PAA addition, 20 Min Contact Time | 2019-06-25 | 11:16 | 6/25/19 11:16 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.68 | 0.68 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 06:53 | 0.79493
012_712_1021 | 2 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-25 | 11:23 | 6/25/19 11:23 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.17 | 0.17 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 06:54 | 0.79461
012_712_1021 | 2 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-25 | 11:23 | 6/25/19 11:23 | TSS | Total Suspended Solids | Total Suspended Solids | 9 | 9 | mg/L | 1 |  | G |  |  |  |  | 2019-06-22 06:55 | 0.64958
012_712_1021 | 2 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-25 | 11:23 | 6/25/19 11:23 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 58 | 58 | EC/100mL | 1 |  | G |  |  |  |  | 2019-06-22 06:56 | 0.64958
012_700_1011 | 2 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-25 | 10:59 | 6/25/19 10:59 | CODLL | CODLL, w/Ag2SO4, w/ HgSO4 | CODLL, w/Ag2SO4, w/ HgSO4 | 23 | 23 | mg/L | 5 |  | G |  |  |  |  | 2019-06-22 06:57 | 0.64958
012_700_1011 | 2 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-25 | 10:59 | 6/25/19 10:59 | DTRM4 | Dig., Tot. Rec. Metals | Dig., Tot. Rec. Metals | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 06:58 | 0.64958
012_700_1011 | 2 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-25 | 10:59 | 6/25/19 10:59 | $ICPT1 | Metals, Tot., ICP | Metals, Tot., ICP | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 06:59 | 0.64958
012_700_1011 | 2 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-25 | 10:59 | 6/25/19 10:59 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 12200 | 12200 | EC/100mL | 100 |  | G |  |  |  |  | 2019-06-22 07:00 | 0.64958
012_700_1011 | 2 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-25 | 10:59 | 6/25/19 10:59 | TSS | Total Suspended Solids | Total Suspended Solids | 12 | 12 | mg/L | 1 |  | G |  |  |  |  | 2019-06-22 07:01 | 0.7926
012_712_1012 | 3 NPAA10MN | RWH North, Post-PAA addition, 10 Min Contact Time | 2019-06-25 | 13:19 | 6/25/19 13:19 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.83 | 0.83 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 07:02 | 0.79224
012_712_1012 | 3 NPAA10MN | RWH North, Post-PAA addition, 10 Min Contact Time | 2019-06-25 | 13:19 | 6/25/19 13:19 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 313 | 313 | EC/100mL | 1 |  | G |  |  |  |  | 2019-06-22 07:03 | 0.79187
012_712_1011 | 3 NPAA1MIN | RWH North, Post-PAA addition, 1 Min Contact Time | 2019-06-25 | 13:09 | 6/25/19 13:09 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 1.25 | 1.25 | mg/L | 0.1 |  | G | 0.88349 | 1.25 | 0.36651 | 85.9036 | 2019-06-22 07:04 | 0.79151
012_712_1011 | 3 NPAA1MIN | RWH North, Post-PAA addition, 1 Min Contact Time | 2019-06-25 | 13:09 | 6/25/19 13:09 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 14700 | 14700 | EC/100mL | 100 |  | G |  |  |  |  | 2019-06-22 07:05 | 0.79115
012_712_1013 | 3 NPAA20MN | RWH North, Post-PAA addition, 20 Min Contact Time | 2019-06-25 | 13:25 | 6/25/19 13:25 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.73 | 0.73 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 07:06 | 0.79078
012_712_1021 | 3 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-25 | 13:33 | 6/25/19 13:33 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 68 | 68 | EC/100mL | 1 |  | G |  |  |  |  | 2019-06-22 07:07 | 0.68332
012_712_1021 | 3 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-25 | 13:33 | 6/25/19 13:33 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.49 | 0.49 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 07:08 | 0.68322
012_712_1021 | 3 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-25 | 13:33 | 6/25/19 13:33 | TSS | Total Suspended Solids | Total Suspended Solids | 8 | 8 | mg/L | 1 |  | G |  |  |  |  | 2019-06-22 07:09 | 0.68322
012_700_1011 | 3 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-25 | 13:02 | 6/25/19 13:02 | CODLL | CODLL, w/Ag2SO4, w/ HgSO4 | CODLL, w/Ag2SO4, w/ HgSO4 | 23 | 23 | mg/L | 5 |  | G |  |  |  |  | 2019-06-22 07:10 | 0.68322
012_700_1011 | 3 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-25 | 13:02 | 6/25/19 13:02 | DTRM4 | Dig., Tot. Rec. Metals | Dig., Tot. Rec. Metals | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:11 | 0.68322
012_700_1011 | 3 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-25 | 13:02 | 6/25/19 13:02 | $ICPT1 | Metals, Tot., ICP | Metals, Tot., ICP | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:12 | 0.68322
012_700_1011 | 3 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-25 | 13:02 | 6/25/19 13:02 | TSS | Total Suspended Solids | Total Suspended Solids | 11 | 11 | mg/L | 1 |  | G |  |  |  |  | 2019-06-22 07:13 | 0.66102
012_700_1011 | 3 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-25 | 13:02 | 6/25/19 13:02 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 15500 | 15500 | EC/100mL | 100 |  | G |  |  |  |  | 2019-06-22 07:14 | 0.65938
011_530_1061 | S_PREPAA | RWH South, Sec Clarifiers, Clar 6 Eff | 2019-06-25 | 07:07 | 6/25/19 07:07 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 105000 | 105000 | EC/100mL | 100 |  | G |  |  |  |  | 2019-06-22 07:15 | 0.66002
012_712_1011 | N_PAA1MIN | RWH North, Post-PAA addition, 1 Min Contact Time | 2019-06-26 | 07:22 | 6/26/19 07:22 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 1.0 | 1.0 | mg/L | 0.1 |  | G | 0.62516 | 1.0 | 0.37484 | 32.5038 | 2019-06-22 07:16 | 0.66065
012_700_1011 | N_PREPAA | RWH North, Pre-PAA addition | 2019-06-26 | 07:20 | 6/26/19 07:20 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 8600 | 8600 | EC/100mL | 100 |  | G |  |  |  |  | 2019-06-22 07:17 | 0.66129
011_530_1061 | S_PREPAA | RWH South, Sec Clarifiers, Clar 6 Eff | 2019-06-26 | 07:15 | 6/26/19 07:15 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | 26100 | 26100 | EC/100mL | 100 |  | G |  |  |  |  | 2019-06-22 07:18 | 0.66193
012_712_1012 | 1 NPAA10MN | RWH North, Post-PAA addition, 10 Min Contact Time | 2019-06-27 | 07:51 | 6/27/19 07:51 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.39 | 0.39 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 07:19 | 0.66256
012_712_1012 | 1 NPAA10MN | RWH North, Post-PAA addition, 10 Min Contact Time | 2019-06-27 | 07:51 | 6/27/19 07:51 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:20 | 0.66328
012_712_1011 | 1 NPAA1MIN | RWH North, Post-PAA addition, 1 Min Contact Time | 2019-06-27 | 07:44 | 6/27/19 07:44 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 1.32 | 1.32 | mg/L | 0.1 |  | G | 0.68009 | 1.32 | 0.63991 | 34.1561 | 2019-06-22 07:21 | 0.66402
012_712_1011 | 1 NPAA1MIN | RWH North, Post-PAA addition, 1 Min Contact Time | 2019-06-27 | 07:44 | 6/27/19 07:44 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:22 | 0.66477
012_712_1013 | 1 NPAA20MN | RWH North, Post-PAA addition, 20 Min Contact Time | 2019-06-27 | 07:57 | 6/27/19 07:57 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.10 | 0.10 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 07:23 | 0.66551
012_712_1021 | 1 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-27 | 08:05 | 6/27/19 08:05 | TSS | Total Suspended Solids | Total Suspended Solids | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:24 | 0.66625
012_712_1021 | 1 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-27 | 08:05 | 6/27/19 08:05 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:25 | 0.66699
012_712_1021 | 1 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-27 | 08:05 | 6/27/19 08:05 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.06 | 0.06 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 07:26 | 0.66774
012_712_1012 | 2 NPAA10MN | RWH North, Post-PAA addition, 10 Min Contact Time | 2019-06-27 | 11:14 | 6/27/19 11:14 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.74 | 0.74 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 07:27 | 0.66848
012_712_1012 | 2 NPAA10MN | RWH North, Post-PAA addition, 10 Min Contact Time | 2019-06-27 | 11:14 | 6/27/19 11:14 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:28 | 0.66922
012_712_1011 | 2 NPAA1MIN | RWH North, Post-PAA addition, 1 Min Contact Time | 2019-06-27 | 11:09 | 6/27/19 11:09 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 1.09 | 1.09 | mg/L | 0.1 |  | G | 0.79629 | 1.09 | 0.29371 | 81.128 | 2019-06-22 07:29 | 0.66996
012_712_1011 | 2 NPAA1MIN | RWH North, Post-PAA addition, 1 Min Contact Time | 2019-06-27 | 11:09 | 6/27/19 11:09 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:30 | 0.66945
012_712_1013 | 2 NPAA20MN | RWH North, Post-PAA addition, 20 Min Contact Time | 2019-06-27 | 11:20 | 6/27/19 11:20 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.64 | 0.64 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 07:31 | 0.66866
012_712_1021 | 2 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-27 | 11:26 | 6/27/19 11:26 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.41 | 0.41 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 07:32 | 0.64958
012_712_1021 | 2 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-27 | 11:26 | 6/27/19 11:26 | TSS | Total Suspended Solids | Total Suspended Solids | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:33 | 0.64958
012_712_1021 | 2 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-27 | 11:26 | 6/27/19 11:26 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:34 | 0.64958
012_700_1011 | 2 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-27 | 11:04 | 6/27/19 11:04 | CODLL | CODLL, w/Ag2SO4, w/ HgSO4 | CODLL, w/Ag2SO4, w/ HgSO4 | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:35 | 0.64958
012_700_1011 | 2 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-27 | 11:04 | 6/27/19 11:04 | DTRM4 | Dig., Tot. Rec. Metals | Dig., Tot. Rec. Metals | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:36 | 0.64958
012_700_1011 | 2 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-27 | 11:04 | 6/27/19 11:04 | $ICPT1 | Metals, Tot., ICP | Metals, Tot., ICP | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:37 | 0.64958
012_700_1011 | 2 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-27 | 11:04 | 6/27/19 11:04 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:38 | 0.71518
012_700_1011 | 2 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-27 | 11:04 | 6/27/19 11:04 | TSS | Total Suspended Solids | Total Suspended Solids | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:39 | 0.71485
012_712_1012 | 3 NPAA10MN | RWH North, Post-PAA addition, 10 Min Contact Time | 2019-06-27 | 13:28 | 6/27/19 13:28 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.96 | 0.96 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 07:40 | 0.71451
012_712_1012 | 3 NPAA10MN | RWH North, Post-PAA addition, 10 Min Contact Time | 2019-06-27 | 13:28 | 6/27/19 13:28 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:41 | 0.71418
012_712_1011 | 3 NPAA1MIN | RWH North, Post-PAA addition, 1 Min Contact Time | 2019-06-27 | 13:22 | 6/27/19 13:22 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 1.18 | 1.18 | mg/L | 0.1 |  | G | 0.87705 | 1.18 | 0.30295 | 83.1776 | 2019-06-22 07:42 | 0.71385
012_712_1011 | 3 NPAA1MIN | RWH North, Post-PAA addition, 1 Min Contact Time | 2019-06-27 | 13:22 | 6/27/19 13:22 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:43 | 0.71346
012_712_1013 | 3 NPAA20MN | RWH North, Post-PAA addition, 20 Min Contact Time | 2019-06-27 | 13:32 | 6/27/19 13:32 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.70 | 0.70 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 07:44 | 0.71287
012_712_1021 | 3 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-27 | 13:38 | 6/27/19 13:38 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:45 | 0.71227
012_712_1021 | 3 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-27 | 13:38 | 6/27/19 13:38 | PAAR | PAA Residual, Peroxychem | PAA Residual, Peroxychem | 0.49 | 0.49 | mg/L | 0.1 |  | G |  |  |  |  | 2019-06-22 07:46 | 0.71168
012_712_1021 | 3 NPAA30MN | RWH North, Post-PAA Pre-SBS, 30 Min Contact Time | 2019-06-27 | 13:38 | 6/27/19 13:38 | TSS | Total Suspended Solids | Total Suspended Solids | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:47 | 0.71109
012_700_1011 | 3 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-27 | 13:18 | 6/27/19 13:18 | CODLL | CODLL, w/Ag2SO4, w/ HgSO4 | CODLL, w/Ag2SO4, w/ HgSO4 | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:48 | 0.71049
012_700_1011 | 3 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-27 | 13:18 | 6/27/19 13:18 | DTRM4 | Dig., Tot. Rec. Metals | Dig., Tot. Rec. Metals | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:49 | 0.7099
012_700_1011 | 3 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-27 | 13:18 | 6/27/19 13:18 | $ICPT1 | Metals, Tot., ICP | Metals, Tot., ICP | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:50 | 0.67581
012_700_1011 | 3 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-27 | 13:18 | 6/27/19 13:18 | TSS | Total Suspended Solids | Total Suspended Solids | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:51 | 0.67551
012_700_1011 | 3 N_PREPAA | RWH North, Pre-PAA addition | 2019-06-27 | 13:18 | 6/27/19 13:18 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:52 | 0.67521
011_530_1061 | S_PREPAA | RWH South, Sec Clarifiers, Clar 6 Eff | 2019-06-27 | 10:08 | 6/27/19 10:08 | ECIDX | E-Coli, MPN Idexx Colilert | E-Coli, MPN Idexx Colilert | PENDING |  |  |  |  | G |  |  |  |  | 2019-06-22 07:53 | 0.67491

## Sheet1
|  | HRT | Actual PAA | Chemscan
2019-06-24 08:00 | N_PrePAA | [5 empty] | 2019-06-24 08:00 | 2019-06-24 11:00 | 2019-06-24 13:02 | 2019-06-25 08:00 | 2019-06-25 11:04 | 2019-06-25 13:09
37.8865 | N_1 Min | 4.1441 | 1.18 |  |  | Chemscan | 0.73045 | 0.85077 | 0.99466 | 0.62516 | 0.70047 | 0.88349
| N_1st Pass-1 | 11.1964
| N_1st Pass-2 | 14.7225 |  |  |  | Flow | 37.8865 | 86.5376 | 100.1685 | 40.8853 | 82.1014 | 85.9036
| N_1st Pass-3 | 18.2487 |  |  |  | Hypothetical HRT | 22.3994 | 17.0877 | 11.0387 | 27.2663 | 23.7633 | 15.6847
| N_1st Pass-4 | 21.7748 |  |  |  |  | 2019-06-24 08:00: a; 2019-06-24 11:00: b; 2019-06-24 13:02: c
| N_1st Pass-5 | 25.301 |  |  |  |  | 2019-06-24 08:00: 0.0001; 2019-06-24 11:00: -0.0266; 2019-06-24 13:02: 1.2761
| N_10 Min | 32.3533 | 0.46 | 0.73045 | -0.27045
| N_2nd Pass-3 | 45.5375 |  |  |  | Flow | 37.8865 | 86.5376 | 100.1685 | 40.8853 | 82.1014 | 85.9036
| N_20 Min | 58.7218 | 0.21 |  |  | Hypothetical HRT |  | 18.733 | 11.5743 | 29.9571 | 26.2107 | 17.1051
| N_3rd Pass-3 | 71.8684 | bar: 2019-06-24 08:00 to 2019-06-24 11:00
| N_30 Min | 85.0151 |  |  |  |  | 2019-06-24 08:00: -0.0201; 2019-06-24 11:00: 1.2273
2019-06-24 11:00 | N_PrePAA
86.5376 | N_1 Min | 1.9204 | 1.21
| N_1st Pass-1 | 5.1125
| N_1st Pass-2 | 6.7085
| N_1st Pass-3 | 8.3045
| N_1st Pass-4 | 9.9006
| N_1st Pass-5 | 11.4966
| N_10 Min | 14.6887 | 0.85 | 0.85077 | -0.00076678
| N_2nd Pass-3 | 20.6524
| N_20 Min | 26.6162 | 0.71
| N_3rd Pass-3 | 32.5591
| N_30 Min | 38.502 | 0.47
2019-06-24 13:02 | N_PrePAA
100.1685 | N_1 Min | 1.6758 | 1.29
| N_1st Pass-1 | 4.4498
| N_1st Pass-2 | 5.8368
| N_1st Pass-3 | 7.2238
| N_1st Pass-4 | 8.6108
| N_1st Pass-5 | 9.9978
| N_10 Min | 12.7718 | 1.07 | 0.99466 | 0.075344
| N_2nd Pass-3 | 17.9539
| N_20 Min | 23.136 | 0.93
| N_3rd Pass-3 | 28.2994
| N_30 Min | 33.4628 | 0.57
2019-06-25 08:00 | N_PrePAA
40.8853 | N_1 Min | 3.8603 | 1.09
| N_1st Pass-1 | 10.4155
| N_1st Pass-2 | 13.6931
| N_1st Pass-3 | 16.9706
| N_1st Pass-4 | 20.2482
| N_1st Pass-5 | 23.5258
| N_10 Min | 30.081 | 0.58 | 0.62516 | -0.045162
| N_2nd Pass-3 | 42.3351
| N_20 Min | 54.5892 | 0.16
| N_3rd Pass-3 | 66.8076
| N_30 Min | 79.026
2019-06-25 11:04 | N_PrePAA
82.1014 | N_1 Min | 2.0168 | 1.24
| N_1st Pass-1 | 5.3743
| N_1st Pass-2 | 7.053
| N_1st Pass-3 | 8.7317
| N_1st Pass-4 | 10.4104
| N_1st Pass-5 | 12.0891
| N_10 Min | 15.4465 | 0.7 | 0.70047 | -0.00046538
| N_2nd Pass-3 | 21.7195
| N_20 Min | 27.9924 | 0.68
| N_3rd Pass-3 | 34.2437
| N_30 Min | 40.495 | 0.17
2019-06-25 13:09 | N_PrePAA
85.9036 | N_1 Min | 1.9336 | 1.25
| N_1st Pass-1 | 5.1483
| N_1st Pass-2 | 6.7556
| N_1st Pass-3 | 8.3629
| N_1st Pass-4 | 9.9703
| N_1st Pass-5 | 11.5776
| N_10 Min | 14.7923 | 0.83 | 0.88349 | -0.053488
| N_2nd Pass-3 | 20.7983
| N_20 Min | 26.8043 | 0.73
| N_3rd Pass-3 | 32.7894
| N_30 Min | 38.7745 | 0.49
Note on D13: Newhart, Kathryn: 0 deleted
Note on D49: Newhart, Kathryn: 0.03 deleted